## Sheet1
.
| Calculating Room Size |  |  |  | Total cu. ft. In room
| Length | Width | Height |  |  |  |  | READ ALL INSTRUCTIONS
| 25 | 40 | 8 |  | 8000
Insert Numbers Then Hit "Enter" Key
| Enter Btu's |  | Total cu. ft. needed |  | Additional cu. ft. needed
| 140000 |  | 7000 |  | -1000
COMBUSTION AIR FROM INSIDE OF BUILDING
Calculation of square inches of Grill Size 1 square inch for every 2000 BTU's
| Using Metal Grill | [5 empty] | Using Wooden Grill
| Square Inches Needed |  | 186.6667 |  |  |  | Square Inches Needed |  | 560
| Size of Metal Grill needed |  | 13.6626 | BY | 13.6626 |  | Size of Wooden Grill Needed |  | 23.6643 | BY | 23.6643
|  |  | 12" x 12" minimum size grill | [5 empty] | 20" x 20 " minimum size grill
Obtaining Outside Combustion Air
| BTU'S | Size of Vertical Round Pipe Size without Grill (one 12" of top & one 12" of bottom) |  |  | Hole Only ----- Sq. Inches of Hole Needed in ceiling and floor or wall Without a Grill 12" of top and one 12" of bottom- Air Openings shall not be less than 3 inches |  |  |  | When Using Metal Grill- Size Needed - (one 12" of top & one 12" of bottom)
| 140000 | Sq. Inches Needed | 35 |  | Hole Size | Sq. Inches Needed | 35 |  | Grill Size | Sq. Inches Needed | 46.6667
| see chart below |  |  |  | 5.9161 | BY | 5.9161 |  | 6.8313 | BY | 6.8313
Obtaining Combustion Air From Outside the Building | One Permanent Opening Installation | [6 empty] | Square Inches of Horizontal Ducts
| 1 square inch per 3000 BTU's (1" clearance on Sides & Back & 6" on Front of appliances) | [6 empty] | 1 square inch per 2000 BTU's Ducts to be Installed Top & Bottom with Metal Grill
| Sq. Inches Needed | 62.2222 | [5 empty] | Sq. Inches Needed | 93.3333
| Opening Size | 7.8881 | BY | 7.8881 |  |  |  | Duct Size | 9.6609 | BY | 9.6609
|  |  |  | Round Pipe Chart without a grill | [7 empty] | .
|  | Total Square Inches Required |  |  | Round Pipe Size |  | Total Square Inches Required |  |  | Round Pipe Size
|  | 0 | thru | 7 | 3" |  | 132.8 | thru | 153.9 | 14"
|  | 7.1 | thru | 12.5 | 4" |  | 154 | thru | 176.7 | 15"
|  | 12.6 | thru | 19.6 | 5" |  | 176.8 | thru | 201 | 16"
|  | 19.7 | thru | 28.2 | 6" |  | 201.1 | thru | 226.9 | 17"
|  | 28.3 | thru | 38.5 | 7" |  | 227 | thru | 254.4 | 18"
|  | 38.6 | thru | 50.3 | 8" |  | 254.5 | thru | 283.5 | 19"
|  | 50.4 | thru | 63.6 | 9" |  | 283.6 | thru | 314.1 | 20"
|  | 63.7 | thru | 78.5 | 10" |  | 314.2 | thru | 346.3 | 21"
|  | 78.6 | thru | 95 | 11" |  | 346.4 | thru | 380.1 | 22"
|  | 95.1 | thru | 113 | 12" |  | 380.2 | thru | 415.4 | 23"
|  | 113.1 | thru | 132.7 | 13" |  | 415..5 | thru | 452.3 | 24"
.